## Tabelle1
Component | C_D+Z (Basecase) | f (Basecase) | C_D+Z (1. Iteration) | f (1. Iteration) | Objective | air ratio | pressure ratio | number of collectors | HRSG Pressure | Pinchpoint Temperature EVAP_HP | OLD Version
Initial Vlaues | [5 empty] | 2.6 | 13 | 25 | 110 | 12 |  |  | ε_k ↑
GT_CC | 3503.2811 | 0.069497 | 3449.699 | 0.065433 | ε_k ↑ | ↓ | ↑ | ↓ | - | ↓ |  |  | Z_k ↓
GT_EXP | 2877.3253 | 0.77565 | 2603.7992 | 0.79466 | Z_k ↓ | ↓ | ↓ | ↑ | ↑ | ↓ |  |  | -
GT_COMP | 1747.7207 | 0.71975 | 1314.9996 | 0.68496 | Z_k ↓ | ↓ | ↑ | ↑ | ↑ | -
LP_ST | 470.3636 | 0.46668 | 516.2223 | 0.46118 | - | - | - | - | - | - |  |  | ↑
EVAP_HP | 509.3383 | 0.49886 | 514.6659 | 0.50943 | Z_k ↓ | ↓ | ↑ | ↑ | ↑ | ↑ |  |  | ↓
SOLARFIELD | 255.4261 | 0.93 | 425.7101 | 0.93 | Z_k ↓ | - | - | ↓ | - | -
GEN_GT | 456.7621 | 0.71071 | 418.0385 | 0.70801 | - | - | - | - | - | -
GEN_ST | 346.028 | 0.74532 | 391.5771 | 0.75293 | - | - | - | - | - | -
SH_HP | 284.815 | 0.49311 | 347.5377 | 0.49709 | ε_k ↑ | ↑ | ↓ | - | ↑ | -
HP_ST | 312.6211 | 0.68365 | 338.9347 | 0.68457 | Z_k ↓ | ↑ | ↑ | - | ↓ | -
sum of C_D+Z (increasing DV) | [5 empty] | 686.4724 | 5965.8368 | 4433.4647 | 4781.0023 | 514.6659
sum of C_D+Z (decreasing DV) | [5 empty] | 7883.1636 | 2951.3369 | 3875.4091 | 338.9347 | 6053.4981
Suggestion | [5 empty] | ↓ | ↑ | ↑ | ↑ | ↓
New Value | [5 empty] | 2.4 | 16 | 35 | 120 | 10
Component | C_D+Z (Basecase) | f (Basecase) | C_D+Z (1. Iteration) | f (1. Iteration) | Objective | air ratio | pressure ratio | number of collectors | HRSG Pressure | Pinchpoint Temperature EVAP_HP
Initial Vlaues | [5 empty] | 2.6 | 13 | 25 | 110 | 12
GT_CC | 4410.0599 | 0.033002 | 3345.0325 | 0.03619 | ε_k ↑ | ↓ | ↑ | - | - | ↓
GT_EXP | 2089.0824 | 0.63862 | 1606.9652 | 0.69055 | Z_k ↓ | ↓ | ↓ | ↑ | ↑ | ↓
GT_COMP | 1290.1244 | 0.58286 | 925.6537 | 0.60694 | Z_k ↓ | ↓ | ↑ | ↑ | ↑ | -
EVAP_HP | 428.7407 | 0.30374 | 369.6732 | 0.36478 | ε_k ↑ | ↓ | ↑ | - | ↓ | ↑ |  | needs to be filled
LP_ST | 369.2793 | 0.31308 | 333.9003 | 0.35453 | ε_k ↑ | ↓ | ↑ | - | ↓ | -
GEN_GT | 339.2392 | 0.57203 | 291.8132 | 0.63264 | - | - | - | - | - | -
SH_HP | 240.8217 | 0.29889 | 251.4118 | 0.35342 | ε_k ↑ | ↑ | ↓ | - | ↑ | -
GEN_ST | 213.6711 | 0.61598 | 223.9928 | 0.67103 | - | - | - | - | - | -
SOLARFIELD | 130.2184 | 0.93 | 217.0307 | 0.93 | Z_k ↓ | - | - | ↓ | - | -
HP_ST | 204.6455 | 0.51604 | 208.3372 | 0.57108 | - | - | - | - | - | -
sum of C_D+Z (increasing DV) | [5 empty] | 251.4118 | 4974.2597 | 2532.6189 | 2784.0307 | 369.6732
sum of C_D+Z (decreasing DV) | [5 empty] | 6581.2249 | 1858.377 | 217.0307 | 703.5735 | 4951.9977
Suggestion | [5 empty] | ↓ | ↑ | ↑ | ↑ | ↓
New Value | [5 empty] | 2.4 | 16 | 35 | 120 | 10
Note on H5: User: specific fuel consumption
Note on I5: User: SFC reduces
Note on J5: User: SFC reduces if collector number reduces
Note on H6: User: smaller mass flow, smaller GT
Note on I6: User: smaller mass flow
Note on H7: User: Smaller compressor
Note on I7: User: smaller mass flow but , higher power consumption
Note on L7: User: no significant changes
Note on I9: User: transfer area decreases
Note on H14: User: lower TIT
Note on I14: User: lower TIT
Note on J14: User: no significant changes
Note on K14: User:
Note on L14: User: no significant changes
Note on I17: User: lower TIT
Note on H28: User: specific fuel consumption
Note on I28: User: SFC reduces
Note on J28: User: SFC reduces if collector number reduces
Note on H29: User: smaller mass flow, smaller GT
Note on I29: User: smaller mass flow
Note on H30: User: Smaller compressor
Note on I30: User: smaller mass flow but , higher power consumption
Note on L30: User: no significant changes
Note on J31: Hithesh: area of evap decreaes with increase in Ncoll, but the Q/A is const
Note on I32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Very small change in efficiency on the forth decimal
Note on K32: Hithesh: changes on 3rd decimal
Note on H37: User: lower TIT
Note on I37: User: lower TIT
Note on J37: User: no significant changes
Note on K37: User:
Note on L37: User: no significant changes
Note on I40: User: lower TIT
Note on J40: User: lower TIT

## Sheet1
Component | C_D+Z (Basecase) | f (Basecase) | C_D+Z (1. Iteration) | f (1. Iteration) | Objective | air ratio | pressure ratio | number of collectors | HRSG Pressure | Pinchpoint Temperature EVAP_HP
Initial Vlaues | [5 empty] | 2.6 | 13 | 25 | 110 | 12
GT_CC | 4410.0599 | 0.033002 | 3345.0325 | 0.03619 | ε_k ↑ | ↓ | ↑ | - | - | ↓
GT_EXP | 2089.0824 | 0.63862 | 1606.9652 | 0.69055 | Z_k ↓ | ↑ | ↓ | ↑ | ↑ | ↓
GT_COMP | 1290.1244 | 0.58286 | 925.6537 | 0.60694 | Z_k ↓ | ↓ | ↓ | ↑ | ↑ | ↓
EVAP_HP | 428.7407 | 0.30374 | 369.6732 | 0.36478 | ε_k ↑ | ↓ | ↓ | - | ↓ | ↓
LP_ST | 369.2793 | 0.31308 | 333.9003 | 0.35453 | ε_k ↑ | - | - | - | ↓ | -
GEN_GT | 339.2392 | 0.57203 | 291.8132 | 0.63264 | - | - | - | - | - | -
SH_HP | 240.8217 | 0.29889 | 251.4118 | 0.35342 | ε_k ↑ | ↓ | ↓ | - | ↑ | -
GEN_ST | 213.6711 | 0.61598 | 223.9928 | 0.67103 | - | - | - | - | - | -
SOLARFIELD | 130.2184 | 0.93 | 217.0307 | 0.93 | Z_k ↓ | - | - | ↓ | - | -
HP_ST | 204.6455 | 0.51604 | 208.3372 | 0.57108 | - | - | - | - | - | -
sum of C_D+Z (increasing DV) | [5 empty] | 1606.9652 | 3345.0325 | 2532.6189 | 2784.0307
sum of C_D+Z (decreasing DV) | [5 empty] | 4891.7711 | 3153.7039 | 217.0307 | 703.5735 | 6247.3246
Suggestion | [5 empty] | ↓ | ↑ | ↑ | ↑ | ↓
New Value | [5 empty] | 2.4 | 16 | 35 | 120 | 10
Note on H6: User: specific fuel consumption
Note on I6: User: SFC reduces
Note on J6: User: SFC reduces if collector number reduces
Note on H7: User: SFC reduces
Note on I7: User: smaller mass flow
Note on H8: User: Smaller compressor
Note on I8: User: smaller mass flow
Note on I9: User: smaller mass flow
Note on J9: Hithesh: area of evap decreaes with increase in Ncoll, but the Q/A is const
Note on K10: Hithesh: changes on 3rd decimal
Note on H12: User: Smaller compressor
Note on H15: User: lower TIT
Note on I15: User: lower TIT
Note on J15: User: no significant changes
Note on K15: User:
Note on L15: User: no significant changes
Note on I18: User: lower TIT
Note on J18: User: lower TIT

## Sheet2
Component | C_D+Z (1st Iteration) | f ( 1st Iteration) | Objective | Air ratio | Pressure ratio | Number of collectors | HRSG Pressure | Pinch point Temperature EVAP_HP
GT_CC | 3345.0325 | 0.03619 | ε_k ↑ | ↓ | ↑ | - | - | ↓
GT_EXP | 1606.9652 | 0.69055 | Z_k ↓ | ↑ | ↓ | ↑ | ↑ | ↓
GT_COMP | 925.6537 | 0.60694 | Z_k ↓ | ↓ | ↓ | ↑ | ↑ | ↓
EVAP_HP | 369.6732 | 0.36478 | ε_k ↑ | ↓ | ↓ | - | ↓ | ↓
LP_ST | 333.9003 | 0.35453 | ε_k ↑ | - | - | - | ↓ | -
GEN_GT | 291.8132 | 0.63264 | - | - | - | - | - | -
SH_HP | 251.4118 | 0.35342 | ε_k ↑ | ↓ | ↓ | - | ↑ | -
GEN_ST | 223.9928 | 0.67103 | - | - | - | - | - | -
SOLARFIELD | 217.0307 | 0.93 | Z_k ↓ | - | - | ↓ | - | -
HP_ST | 208.3372 | 0.57108 | - | - | - | - | - | -
Sum of combined costs (increasing DV) |  |  |  | 1606.9652 | 3345.0325 | 2532.6189 | 2784.0307
Sum of combined costs (decreasing DV) |  |  |  | 4891.7711 | 3153.7039 | 217.0307 | 703.5735 | 6247.3246
Suggestion |  |  |  | ↓ | ↑ | ↑ | ↑ | ↓

## data
Component | C_D+Z (Basecase) [$/h] | f (Basecase) | C_D+Z (1st Iteration) [$/h] | f (1st Iteration)
GT_CC | 4410.0599 | 0.033002 | 3345.0325 | 0.03619
GT_EXP | 2089.0824 | 0.63862 | 1606.9652 | 0.69055
GT_COMP | 1290.1244 | 0.58286 | 925.6537 | 0.60694
EVAP_HP | 428.7407 | 0.30374 | 369.6732 | 0.36478
LP_ST | 369.2793 | 0.31308 | 333.9003 | 0.35453
GEN_GT | 339.2392 | 0.57203 | 291.8132 | 0.63264
SH_HP | 240.8217 | 0.29889 | 251.4118 | 0.35342
GEN_ST | 213.6711 | 0.61598 | 223.9928 | 0.67103
SOLARFIELD | 130.2184 | 0.93 | 217.0307 | 0.93
HP_ST | 204.6455 | 0.51604 | 208.3372 | 0.57108
Total System | 9520.95 | 0.39 | 7777.53 | 0.44

## data2
Comparision Parameters | Base Case | 1st Iterarion
Specific Investment cost $/MW_ex | 928005.215 | 865704.758
Levelized Prooduct Cost $/MWh] | 93.375 | 91.4029
Electric Efficiency | 54.6% | 55.4%
Overall Efficiency | 60.3% | 61.2%

## data4
Cases | Specific Investment cost $/MW_ex | Levelized Prooduct Cost $/MWh] | Electric Efficiency | Overall Efficiency
Base Case | 928005.215 | 93.375 | 54.6% | 60.3%
1st Iteration | 865704.758 | 91.4029 | 55.4% | 61.2%